Annual Drinking Water Quality Report

SHIRLEY WATER DEPARTMENT

(IN5233013)

We're pleased to present to you this year's Annual Quality Water Report. This report is designed to inform you about the quality water and services we deliver to you every day. Our constant goal is to provide you with a safe and dependable supply of drinking water. We want you to understand the efforts we make to continually improve the water treatment process and protect our water resources. We are committed to ensuring the quality of your water. Our water source is ground water which is pumped by three wells from an underground aquifer.

Source Water Information

Source Water Name                                              Type of Water                       Report Status           Location

Well #1                                                                         GW                                     Active                Town Park

Well #2                                                                         GW                                     Active                Town Park

Well #3                                                                         GW                                     Active                Town Park

We have a source water assessment plan available from our office that provides more information such as potential sources of contamination.

I'm pleased to report that our drinking water is safe and meets federal and state requirements.

If you have any questions about this report or concerning your water utility, please contact Nicole Alexander at (765-738-6561).

We want our valued customers to be informed about their water utility. If you want to learn more, please attend any of our regularly scheduled meetings. They are held on the first Monday of each month at 6:30pm in the Town Hall located at 409 Main Street.

The Shirley Water Department routinely monitors for constituents in your drinking water according to Federal and State laws. This table shows the results of our monitoring for the period of January 1st to December 31st, 2020.  As water travels over the land or underground, it can pick up substances or contaminants such as microbes, inorganic and organic chemicals, and radioactive substances.  All drinking water, including bottled drinking water, may be reasonably expected to contain at least small amounts of some constituents.  It's important to remember that the presence of these constituents does not necessarily pose a health risk.

In this table you will find many terms and abbreviations you might not be familiar with. To help you better understand these terms we've provided the following definitions:

Non-Detects (ND) - laboratory analysis indicates that the constituent is not present.

Parts per million (ppm) or Milligrams per liter (mg/l) - one part per million corresponds to one minute in two years or a single penny in $10,000.

Parts per billion (ppb) or Micrograms per liter - one part per billion corresponds to one minute in 2,000 years, or a single penny in $10,000,000.

Picocuries per liter (pCi/L) - picocuries per liter is a measure of the radioactivity in water.

Millirems per year (mrem/yr) - measure of radiation absorbed by the body.

Level 1 Assessment - Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.

Level 2 Assessment –  A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.

Treatment Technique (TT) - A treatment technique is a required process intended to reduce the level of a contaminant in drinking water.

Maximum Contaminant Level (MCL) - The “Maximum Allowed” (MCL) is the highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal (MCLG) - The “Goal”(MCLG) is the level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs allow for a margin of safety.

Maximum Residual Disinfectant Level (MRDL) – The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

Maximum Residual Disinfectant Level Goal (MRDLG) – The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

| TEST RESULTS |
| --- |
| Contaminant | Violation Y/N | Highest Level Detected | Range of Levels Detected | Unit Measurement | MCLG | MCL | Likely Source of Contamination |
| Radioactive Contaminants |
| Gross Alpha emitters excluding radon and uranium (Tested 2017) | N | 0.4 | 0.4-0.4 | pCi/1 | 0 | 15 | Erosion of natural deposits |
| Uranium (Tested 2017) | N | 0.2931 | 0.2931-0.2931 | µg/L | 0 | 30 | Erosion of natural deposits |
| Inorganic Contaminants |
| Arsenic (Tested 2018) | N | 0.8 | 0.8-0.8 | ppb | 0 | 10 | Erosion of natural deposits; runoff from orchards; runoff from glass and electronics production wastes |
| Barium (Tested 2018) | N | 0.209 | 0.209-0.209 | ppm | 2 | 2 | Discharge of drilling wastes; discharge from metal refineries; erosion of natural deposits |
| Fluoride (Tested 2018) | N | 1.3 | 1.3-1.3 | ppm | 4 | 4 | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories |
| Nickel (Tested 2018) | N | 0.0017 | 0.0017-0.0017 | ppm | 0 | 100 | Possible waste runoff from industry |
| Nitrate (as Nitrogen) (Tested 2020) | N | 0.692 | 0.692 – 0.692 | ppm | 10 | 10 | Runoff from fertilizer use; leaching from septic tanks, sewage; erosion of natural deposits |

Synthetic Organic Compounds (Tested 2019), (Non Detects)

Volatile Organic Contaminants (Tested 2018), (Non Detects)

Disinfection and Disinfection Byproducts

| Chlorine (Tested 2020) | N | 1.0 | 1.0 – 1.0 | ppm | 4.0 | 4.0 | Water additive used to control microbes. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TTHM [Total trihalomethanes] (Tested 2020) | N | 25.0 | 25.2 – 25.2 | ppb | No Goal for Total | 80 | By-product of drinking water chlorination |
| Total HAA5’s [Halocetic Acids] (Tested 2020) | N | 14.0 | 14.0 – 14.0 | ppb | No Goal for Total | 60 | By-product of drinking water chlorination |
| Not all sample results may have been used for calculating the Highest Level Detected because some results may be part of an evaluation to determine where compliance sampling should occur in the future. |

While your drinking water meets EPA’s standard for arsenic, it does contain low levels of arsenic.  EPA’s standard balances the current understanding of arsenic’s possible health effects against the cost of removing arsenic from drinking water.  EPA continues to research the health effects of low levels of arsenic, which is a mineral known to cause cancer in humans at high concentrations and is linked to other health effects such as skin damage and circulatory problems.

LEAD AND COPPER

Definitions:

Action Level Goal (ALG) – The level of a contaminate in drinking water below which there is no known or expected risk to health. ALGs allow for a margin of safety.

Action Level – The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

“If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. The Shirley Water Department is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been setting for several hours, you can minimize the potential of lead exposure by flushing your tap for 30 seconds to 2 minutes before using the water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at http://www.epa.gov/safewater/lead.”

| Lead and Copper | Date Sampled | MCLG | Action Level (AL) | 90th Percentile | # Sites Over AL | Units | Violation | Likely Source of Contamination |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Copper | 2020 | 1.3 | 1.3 | 0.394 | 0 | ppm | N | Erosion of natural deposits; Leaching from wood preservatives; Corrosion of household plumbing systems. |
| Lead | 2020 | 0 | 15 | 8.4 | 0 | ppb | N | Corrosion of household plumbing systems; Erosion of natural deposits. |

As you can see by the table, our system had no violations. We’re proud that your drinking water meets or exceeds all Federal and State requirements. We have learned through our monitoring and testing that some constituents have been detected. The EPA has determined that your water IS SAFE at these levels.

All sources of drinking water are subject to potential contamination by substances that are naturally occurring or man made. These substances can be microbes, inorganic or organic chemicals and radioactive substances. All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water  Hotline at 1-800-426-4791.

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity. Contaminants that may be present in source water include:

* Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

* Inorganic contaminants, such as salts and metals, which can be naturally-occurring or result from urban storm runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

* Pesticides and herbicides, which may come from a variety of sources such as agriculture, stormwater runoff, and residential uses.

* Organic chemicals, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, and septic systems.

* Radioactive materials, which can be naturally-occurring or be the result of oil and gas production and mining activities.

In order to ensure tap water is safe to drink, EPA prescribes regulations that limit the amount of certain contaminants in water provided by public water systems. Food and Drug Administration (FDA) regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

Contaminants may be found in drinking water that may cause taste, color, or odor problems.  These types of problems are not necessarily causes for health concerns.  For more information on taste, odor, or color of drinking water, please contact the system's business office.

MCL’s are set at very stringent levels. To understand the possible health effects described for many regulated constituents, a person would have to drink 2 liters of water every day at the MCL level for a lifetime to have a one-in-a-million chance of having the described health effect.

Nitrates: As a precaution we always notify physicians and health care providers in this area if there is ever a higher than normal level of nitrates in the water supply.

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by cryptosporidium and other microbiological contaminants are available from the Safe Drinking Water Hotline (800-426-4791).

We at Shirley Water Department work around the clock to provide top quality water to every tap, said Jeff Lane the towns certified opeartor. We ask that all our customers help us protect our water sources, which are the heart of our community, our way of life and our children’s future.